## change
idfobject | name | objectfield | value
People | change all | Thermal_Comfort_Model_1_Type | Fanger
People | change all | Work_Efficiency_Schedule_Name | always_off
People | change all | Air_Velocity_Schedule_Name | always_off
People | change all | Clothing_Insulation_Calculation_Method | DynamicClothingModelASHRAE55
HVACTemplate:Zone:IdealLoadsAirSystem | change all | System_Availability_Schedule_Name | HVAC_Sch_<hvac zone no.>

## create
object number | idfobject | objectfield | value
1 | AirflowNetwork:SimulationControl | Name | NV
1 | AirflowNetwork:SimulationControl | AirflowNetwork_Control | MultizoneWithoutDistribution
1 | AirflowNetwork:SimulationControl | Height_Selection_for_Local_Wind_Pressure_Calculation | OpeningHeight
1 | AirflowNetwork:SimulationControl | Building_Type | HighRise
1 | AirflowNetwork:SimulationControl | Wind_Pressure_Coefficient_Type | Input
2 | AirflowNetwork:MultiZone:Zone | Zone_Name | <hvac zone name>
2 | AirflowNetwork:MultiZone:Zone | Ventilation_Control_Mode | Constant
2 | AirflowNetwork:MultiZone:Zone | Venting_Availability_Schedule_Name | NV_Sch_<hvac zone no.>
3 | AirflowNetwork:MultiZone:Zone | Zone_Name | <non-hvac zone name>
3 | AirflowNetwork:MultiZone:Zone | Ventilation_Control_Mode | Constant
3 | AirflowNetwork:MultiZone:Zone | Venting_Availability_Schedule_Name | always_avail
4 | Schedule:Constant | Name | HVAC_Sch_<hvac zone no.>
4 | Schedule:Constant | Schedule_Type_Limits_Name | On/Off
4 | Schedule:Constant | Hourly_Value | 1
5 | Schedule:Constant | Name | NV_Sch_<hvac zone no.>
5 | Schedule:Constant | Schedule_Type_Limits_Name | On/Off
5 | Schedule:Constant | Hourly_Value | 0
6 | EnergyManagementSystem:Sensor | Name | Sensor_out
6 | EnergyManagementSystem:Sensor | OutputVariable_or_OutputMeter_Index_Key_Name | Environment
6 | EnergyManagementSystem:Sensor | OutputVariable_or_OutputMeter_Name | Site Outdoor Air Drybulb Temperature
7 | EnergyManagementSystem:Sensor | Name | Sensor_heat
7 | EnergyManagementSystem:Sensor | OutputVariable_or_OutputMeter_Index_Key_Name | heating_sch
7 | EnergyManagementSystem:Sensor | OutputVariable_or_OutputMeter_Name | Schedule Value
8 | EnergyManagementSystem:Sensor | Name | Sensor_cool
8 | EnergyManagementSystem:Sensor | OutputVariable_or_OutputMeter_Index_Key_Name | cooling_sch
8 | EnergyManagementSystem:Sensor | OutputVariable_or_OutputMeter_Name | Schedule Value
9 | EnergyManagementSystem:Sensor | Name | Sensor_in_<hvac zone no.>
9 | EnergyManagementSystem:Sensor | OutputVariable_or_OutputMeter_Index_Key_Name | <hvac zone name>
9 | EnergyManagementSystem:Sensor | OutputVariable_or_OutputMeter_Name | Zone Operative Temperature
10 | EnergyManagementSystem:Sensor | Name | Sensor_comf_Fan_<hvac zone no.>
10 | EnergyManagementSystem:Sensor | OutputVariable_or_OutputMeter_Index_Key_Name | <people object name>
10 | EnergyManagementSystem:Sensor | OutputVariable_or_OutputMeter_Name | Zone Thermal Comfort Fanger Model PPD
11 | EnergyManagementSystem:Actuator | Name | Control_HVAC_<hvac zone no.>
11 | EnergyManagementSystem:Actuator | Actuated_Component_Unique_Name | HVAC_Sch_<hvac zone no.>
11 | EnergyManagementSystem:Actuator | Actuated_Component_Type | Schedule:Constant
11 | EnergyManagementSystem:Actuator | Actuated_Component_Control_Type | Schedule Value
12 | EnergyManagementSystem:Actuator | Name | Control_NV_<hvac zone no.>
12 | EnergyManagementSystem:Actuator | Actuated_Component_Unique_Name | NV_Sch_<hvac zone no.>
12 | EnergyManagementSystem:Actuator | Actuated_Component_Type | Schedule:Constant
12 | EnergyManagementSystem:Actuator | Actuated_Component_Control_Type | Schedule Value
13 | EnergyManagementSystem:Actuator | Name | Control_Win_<window no.>
13 | EnergyManagementSystem:Actuator | Actuated_Component_Unique_Name | <window name>
13 | EnergyManagementSystem:Actuator | Actuated_Component_Type | AirFlow Network Window/Door Opening
13 | EnergyManagementSystem:Actuator | Actuated_Component_Control_Type | Venting Opening Factor
14 | EnergyManagementSystem:ProgramCallingManager | Name | Calculate_openings_<hvac zone no.>
14 | EnergyManagementSystem:ProgramCallingManager | EnergyPlus_Model_Calling_Point | BeginTimestepBeforePredictor
14 | EnergyManagementSystem:ProgramCallingManager | Program_Name_1 | DefineOpening_<hvac zone no.>
15 | AirflowNetwork:MultiZone:ExternalNode | Name | Node_<surface no.>
15 | AirflowNetwork:MultiZone:ExternalNode | Wind_Pressure_Coefficient_Curve_Name | <wind pressure coefficient curve name>
16 | AirflowNetwork:MultiZone:Surface:Crack | Name | <Crack_non-fen. surface type>
17 | AirflowNetwork:MultiZone:Component:DetailedOpening | Name | <Opening_fen. surface type>
17 | AirflowNetwork:MultiZone:Component:DetailedOpening | Extra_Crack_Length_or_Height_of_Pivoting_Axis | 0
17 | AirflowNetwork:MultiZone:Component:DetailedOpening | Number_of_Sets_of_Opening_Factor_Data | 2
17 | AirflowNetwork:MultiZone:Component:DetailedOpening | Opening_Factor_1 | 0
17 | AirflowNetwork:MultiZone:Component:DetailedOpening | Discharge_Coefficient_for_Opening_Factor_1 | 0.6
17 | AirflowNetwork:MultiZone:Component:DetailedOpening | Width_Factor_for_Opening_Factor_1 | 0
17 | AirflowNetwork:MultiZone:Component:DetailedOpening | Height_Factor_for_Opening_Factor_1 | 0
17 | AirflowNetwork:MultiZone:Component:DetailedOpening | Start_Height_Factor_for_Opening_Factor_1 | 0
17 | AirflowNetwork:MultiZone:Component:DetailedOpening | Opening_Factor_2 | 1
17 | AirflowNetwork:MultiZone:Component:DetailedOpening | Discharge_Coefficient_for_Opening_Factor_2 | 0.6
17 | AirflowNetwork:MultiZone:Component:DetailedOpening | Width_Factor_for_Opening_Factor_2 | 1
17 | AirflowNetwork:MultiZone:Component:DetailedOpening | Height_Factor_for_Opening_Factor_2 | 1
17 | AirflowNetwork:MultiZone:Component:DetailedOpening | Start_Height_Factor_for_Opening_Factor_2 | 0
18 | AirflowNetwork:MultiZone:Surface | Surface_Name | <surface name>
18 | AirflowNetwork:MultiZone:Surface | Leakage_Component_Name | Crack_ or Opening_<surface type>
18 | AirflowNetwork:MultiZone:Surface | External_Node_Name | Node_<surface no.>
18 | AirflowNetwork:MultiZone:Surface | Ventilation_Control_Mode | Constant
18 | AirflowNetwork:MultiZone:Surface | Venting_Availability_Schedule_Name | <venting availability>

## AFN
surface group | energy standard BuildME | energy standard Design Builder | variable | objectfield | value | unit
Windows external | ZEB | Medium | coefficient | Air_Mass_Flow_Coefficient_When_Opening_is_Closed | 0.00014 | kg/s.m crack
Windows external | efficient | Medium/Poor | coefficient | Air_Mass_Flow_Coefficient_When_Opening_is_Closed | 0.00057 | kg/s.m crack
Windows external | standard | Poor | coefficient | Air_Mass_Flow_Coefficient_When_Opening_is_Closed | 0.001 | kg/s.m crack
Windows external | non-standard | Very poor | coefficient | Air_Mass_Flow_Coefficient_When_Opening_is_Closed | 0.003 | kg/s.m crack
Windows internal | ZEB | Medium | coefficient | Air_Mass_Flow_Coefficient_When_Opening_is_Closed | 0.0014 | kg/s.m crack
Windows internal | efficient | Medium/Poor | coefficient | Air_Mass_Flow_Coefficient_When_Opening_is_Closed | 0.0016 | kg/s.m crack
Windows internal | standard | Poor | coefficient | Air_Mass_Flow_Coefficient_When_Opening_is_Closed | 0.0018 | kg/s.m crack
Windows internal | non-standard | Very poor | coefficient | Air_Mass_Flow_Coefficient_When_Opening_is_Closed | 0.003 | kg/s.m crack
Doors external | ZEB | Medium | coefficient | Air_Mass_Flow_Coefficient_When_Opening_is_Closed | 0.00014 | kg/s.m crack
Doors external | efficient | Medium/Poor | coefficient | Air_Mass_Flow_Coefficient_When_Opening_is_Closed | 0.00097 | kg/s.m crack
Doors external | standard | Poor | coefficient | Air_Mass_Flow_Coefficient_When_Opening_is_Closed | 0.0018 | kg/s.m crack
Doors external | non-standard | Very poor | coefficient | Air_Mass_Flow_Coefficient_When_Opening_is_Closed | 0.003 | kg/s.m crack
Doors internal | ZEB | Medium | coefficient | Air_Mass_Flow_Coefficient_When_Opening_is_Closed | 0.02 | kg/s.m crack
Doors internal | efficient | Medium/Poor | coefficient | Air_Mass_Flow_Coefficient_When_Opening_is_Closed | 0.02 | kg/s.m crack
Doors internal | standard | Poor | coefficient | Air_Mass_Flow_Coefficient_When_Opening_is_Closed | 0.02 | kg/s.m crack
Doors internal | non-standard | Very poor | coefficient | Air_Mass_Flow_Coefficient_When_Opening_is_Closed | 0.02 | kg/s.m crack
Vents external | ZEB | Medium | coefficient | Air_Mass_Flow_Coefficient_When_Opening_is_Closed | 0.008 | kg/s.m crack
Vents external | efficient | Medium/Poor | coefficient | Air_Mass_Flow_Coefficient_When_Opening_is_Closed | 0.009 | kg/s.m crack
Vents external | standard | Poor | coefficient | Air_Mass_Flow_Coefficient_When_Opening_is_Closed | 0.01 | kg/s.m crack
Vents external | non-standard | Very poor | coefficient | Air_Mass_Flow_Coefficient_When_Opening_is_Closed | 0.04 | kg/s.m crack
Vents internal | ZEB | Medium | coefficient | Air_Mass_Flow_Coefficient_When_Opening_is_Closed | 0.007 | kg/s.m crack
Vents internal | efficient | Medium/Poor | coefficient | Air_Mass_Flow_Coefficient_When_Opening_is_Closed | 0.008 | kg/s.m crack
Vents internal | standard | Poor | coefficient | Air_Mass_Flow_Coefficient_When_Opening_is_Closed | 0.009 | kg/s.m crack
Vents internal | non-standard | Very poor | coefficient | Air_Mass_Flow_Coefficient_When_Opening_is_Closed | 0.02 | kg/s.m crack
Walls internal | ZEB | Medium | coefficient | Air_Mass_Flow_Coefficient_at_Reference_Conditions | 0.003 | kg/s.m2
Walls internal | efficient | Medium/Poor | coefficient | Air_Mass_Flow_Coefficient_at_Reference_Conditions | 0.004 | kg/s.m2
Walls internal | standard | Poor | coefficient | Air_Mass_Flow_Coefficient_at_Reference_Conditions | 0.005 | kg/s.m2
Walls internal | non-standard | Very poor | coefficient | Air_Mass_Flow_Coefficient_at_Reference_Conditions | 0.019 | kg/s.m2
Walls external | ZEB | Medium | coefficient | Air_Mass_Flow_Coefficient_at_Reference_Conditions | 0.0001 | kg/s.m2
Walls external | efficient | Medium/Poor | coefficient | Air_Mass_Flow_Coefficient_at_Reference_Conditions | 0.00015 | kg/s.m2
Walls external | standard | Poor | coefficient | Air_Mass_Flow_Coefficient_at_Reference_Conditions | 0.0002 | kg/s.m2
Walls external | non-standard | Very poor | coefficient | Air_Mass_Flow_Coefficient_at_Reference_Conditions | 0.0004 | kg/s.m2
Floors internal | ZEB | Medium | coefficient | Air_Mass_Flow_Coefficient_at_Reference_Conditions | 0.0009 | kg/s.m2
Floors internal | efficient | Medium/Poor | coefficient | Air_Mass_Flow_Coefficient_at_Reference_Conditions | 0.00145 | kg/s.m2
Floors internal | standard | Poor | coefficient | Air_Mass_Flow_Coefficient_at_Reference_Conditions | 0.002 | kg/s.m2
Floors internal | non-standard | Very poor | coefficient | Air_Mass_Flow_Coefficient_at_Reference_Conditions | 0.003 | kg/s.m2
Floors external | ZEB | Medium | coefficient | Air_Mass_Flow_Coefficient_at_Reference_Conditions | 0.0007 | kg/s.m2
Floors external | efficient | Medium/Poor | coefficient | Air_Mass_Flow_Coefficient_at_Reference_Conditions | 0.00085 | kg/s.m2
Floors external | standard | Poor | coefficient | Air_Mass_Flow_Coefficient_at_Reference_Conditions | 0.001 | kg/s.m2
Floors external | non-standard | Very poor | coefficient | Air_Mass_Flow_Coefficient_at_Reference_Conditions | 0.002 | kg/s.m2
Roofs | ZEB | Medium | coefficient | Air_Mass_Flow_Coefficient_at_Reference_Conditions | 0.0001 | kg/s.m2
Roofs | efficient | Medium/Poor | coefficient | Air_Mass_Flow_Coefficient_at_Reference_Conditions | 0.000125 | kg/s.m2
Roofs | standard | Poor | coefficient | Air_Mass_Flow_Coefficient_at_Reference_Conditions | 0.00015 | kg/s.m2
Roofs | non-standard | Very poor | coefficient | Air_Mass_Flow_Coefficient_at_Reference_Conditions | 0.0002 | kg/s.m2
Windows external | ZEB | Medium | exponent | Air_Mass_Flow_Exponent_When_Opening_is_Closed | 0.65 | -
Windows external | efficient | Medium/Poor | exponent | Air_Mass_Flow_Exponent_When_Opening_is_Closed | 0.625 | -
Windows external | standard | Poor | exponent | Air_Mass_Flow_Exponent_When_Opening_is_Closed | 0.6 | -
Windows external | non-standard | Very poor | exponent | Air_Mass_Flow_Exponent_When_Opening_is_Closed | 0.6 | -
Windows internal | ZEB | Medium | exponent | Air_Mass_Flow_Exponent_When_Opening_is_Closed | 0.65 | -
Windows internal | efficient | Medium/Poor | exponent | Air_Mass_Flow_Exponent_When_Opening_is_Closed | 0.625 | -
Windows internal | standard | Poor | exponent | Air_Mass_Flow_Exponent_When_Opening_is_Closed | 0.6 | -
Windows internal | non-standard | Very poor | exponent | Air_Mass_Flow_Exponent_When_Opening_is_Closed | 0.6 | -
Doors external | ZEB | Medium | exponent | Air_Mass_Flow_Exponent_When_Opening_is_Closed | 0.65 | -
Doors external | efficient | Medium/Poor | exponent | Air_Mass_Flow_Exponent_When_Opening_is_Closed | 0.655 | -
Doors external | standard | Poor | exponent | Air_Mass_Flow_Exponent_When_Opening_is_Closed | 0.66 | -
Doors external | non-standard | Very poor | exponent | Air_Mass_Flow_Exponent_When_Opening_is_Closed | 0.66 | -
Doors internal | ZEB | Medium | exponent | Air_Mass_Flow_Exponent_When_Opening_is_Closed | 0.6 | -
Doors internal | efficient | Medium/Poor | exponent | Air_Mass_Flow_Exponent_When_Opening_is_Closed | 0.6 | -
Doors internal | standard | Poor | exponent | Air_Mass_Flow_Exponent_When_Opening_is_Closed | 0.6 | -
Doors internal | non-standard | Very poor | exponent | Air_Mass_Flow_Exponent_When_Opening_is_Closed | 0.6 | -
Vents external | ZEB | Medium | exponent | Air_Mass_Flow_Exponent_When_Opening_is_Closed | 0.66 | -
Vents external | efficient | Medium/Poor | exponent | Air_Mass_Flow_Exponent_When_Opening_is_Closed | 0.66 | -
Vents external | standard | Poor | exponent | Air_Mass_Flow_Exponent_When_Opening_is_Closed | 0.66 | -
Vents external | non-standard | Very poor | exponent | Air_Mass_Flow_Exponent_When_Opening_is_Closed | 0.66 | -
Vents internal | ZEB | Medium | exponent | Air_Mass_Flow_Exponent_When_Opening_is_Closed | 0.6 | -
Vents internal | efficient | Medium/Poor | exponent | Air_Mass_Flow_Exponent_When_Opening_is_Closed | 0.6 | -
Vents internal | standard | Poor | exponent | Air_Mass_Flow_Exponent_When_Opening_is_Closed | 0.6 | -
Vents internal | non-standard | Very poor | exponent | Air_Mass_Flow_Exponent_When_Opening_is_Closed | 0.6 | -
Walls internal | ZEB | Medium | exponent | Air_Mass_Flow_Exponent | 0.75 | -
Walls internal | efficient | Medium/Poor | exponent | Air_Mass_Flow_Exponent | 0.75 | -
Walls internal | standard | Poor | exponent | Air_Mass_Flow_Exponent | 0.75 | -
Walls internal | non-standard | Very poor | exponent | Air_Mass_Flow_Exponent | 0.75 | -
Walls external | ZEB | Medium | exponent | Air_Mass_Flow_Exponent | 0.7 | -
Walls external | efficient | Medium/Poor | exponent | Air_Mass_Flow_Exponent | 0.7 | -
Walls external | standard | Poor | exponent | Air_Mass_Flow_Exponent | 0.7 | -
Walls external | non-standard | Very poor | exponent | Air_Mass_Flow_Exponent | 0.7 | -
Floors internal | ZEB | Medium | exponent | Air_Mass_Flow_Exponent | 0.7 | -
Floors internal | efficient | Medium/Poor | exponent | Air_Mass_Flow_Exponent | 0.7 | -
Floors internal | standard | Poor | exponent | Air_Mass_Flow_Exponent | 0.7 | -
Floors internal | non-standard | Very poor | exponent | Air_Mass_Flow_Exponent | 0.7 | -
Floors external | ZEB | Medium | exponent | Air_Mass_Flow_Exponent | 1 | -
Floors external | efficient | Medium/Poor | exponent | Air_Mass_Flow_Exponent | 1 | -
Floors external | standard | Poor | exponent | Air_Mass_Flow_Exponent | 1 | -
Floors external | non-standard | Very poor | exponent | Air_Mass_Flow_Exponent | 1 | -
Roofs | ZEB | Medium | exponent | Air_Mass_Flow_Exponent | 0.7 | -
Roofs | efficient | Medium/Poor | exponent | Air_Mass_Flow_Exponent | 0.7 | -
Roofs | standard | Poor | exponent | Air_Mass_Flow_Exponent | 0.7 | -
Roofs | non-standard | Very poor | exponent | Air_Mass_Flow_Exponent | 0.7 | -

## EMS program
idfobject | objectfield | value
EnergyManagementSystem:Program | Name | DefineOpening_X
EnergyManagementSystem:Program | Program_Line_1 | IF (Sensor_in_X < Sensor_heat)
EnergyManagementSystem:Program | Program_Line_2 | SET Control_HVAC_X = 1
EnergyManagementSystem:Program | Program_Line_3 | SET Control_NV_X = 0
EnergyManagementSystem:Program | Program_Line_<next> | SET Control_<windows> = 0
EnergyManagementSystem:Program | Program_Line_<next> | ELSEIF (Sensor_in_X < Sensor_cool)
EnergyManagementSystem:Program | Program_Line_<next> | SET Control_HVAC_X = 0
EnergyManagementSystem:Program | Program_Line_<next> | SET Control_NV_X = 0
EnergyManagementSystem:Program | Program_Line_<next> | SET Control_<windows> = 0
EnergyManagementSystem:Program | Program_Line_<next> | ELSE
EnergyManagementSystem:Program | Program_Line_<next> | IF (Sensor_in_X > Sensor_out) && (Sensor_comf_Fan_X < 20)
EnergyManagementSystem:Program | Program_Line_<next> | SET Control_HVAC_X = 0
EnergyManagementSystem:Program | Program_Line_<next> | SET Control_NV_X = 1
EnergyManagementSystem:Program | Program_Line_<next> | SET Control_<windows> = 0.27
EnergyManagementSystem:Program | Program_Line_<next> | ELSE
EnergyManagementSystem:Program | Program_Line_<next> | SET Control_HVAC_X = 1
EnergyManagementSystem:Program | Program_Line_<next> | SET Control_NV_X = 0
EnergyManagementSystem:Program | Program_Line_<next> | SET Control_<windows> = 0
EnergyManagementSystem:Program | Program_Line_<next> | ENDIF
EnergyManagementSystem:Program | Program_Line_<next> | ENDIF